## Website Page
PVC Pipe Design Information
Changing Direction by Angular Deflection of Gasketed Pipe Joints
Joint Deflection Design Aid
Instructions
Fill in the three yellow-shaded boxes:
1. Total angle to be turned
2. Allowable angle per joint (as shown in the literature of the manufacturer of the pipe to be used)
3. Pipe laying length (typically 20 feet, but shorter lengths can be ordered to reduce bending radius)
Calculations
|  |  | Total angle to be turned | 0 | degrees
|  |  | Allowable angle per joint | 0 | degrees (per pipe manufacturer's literature)
|  |  | Number of joints | #DIV/0! | CALCULATED
NOTE: If the calculated number of joints is not a whole number, it must be increased to the next largest
whole number. There will be an associated change in total angle to be turned or in the angular
deflection at each joint. For example, if the desired total angle is 5 degrees and the allowable angle
per joint is 1.5 degrees, the number of joints will be calculated at 3.3. This value must be raised to 4.
The total angle turned would increase to 4 x 1.5° = 6.0°; alternatively, the angle turned at each joint
would be reduced to 5.0 / 4 = 1.25° per joint.
|  |  | Pipe laying length | 0 | feet (typically 20 feet)
|  |  | Offset from line of previous pipe segment | 0 | inches | CALCULATED
|  |  | Radius of curvature | #DIV/0! | feet | CALCULATED
Notes
1. The item titled "Offset from line of previous pipe segment" is repeatable for each stick of pipe.
2. In the tables below, enter a value for the pipe laying length. Each value in the column titled
"Offset" is the total offset from the original straight line of pipe prior to beginning angular offsets
(line A-A in the figure).